QUESTION & ANSWER BOARD

Complete Record of Public Questions and Answers

CUH 4.219 Microbiology Lab Expansion Phase II (BSL-3)

Solicitation No. FY2026-RFP-HC-00195

| Source | JAGGAER Public Question & Answer Board |
| --- | --- |
| Total Q&A Entries | 153 |
| Record Captured | August 26, 2026 |
| Prepared For | Source Building Group |

Entries are listed in the order presented on the Q&A board (most recently asked first).

# Index of Questions

1.  Outdated Part Numbers

2.  Security Device Model Numbers

3.  "KP" Security Keypad

4.  Access Control Panels/Power Supplies

5.  IDF Closet Location

6.  Licensing for VMS

7.  Lenel Licensing Confirmation

8.  Panel H4CA

9.  Construction Schedule - Pricing & Delivery

10.  Alternates

11.  Curtain Track

12.  Alternates

13.  Roof Tie Back Anchor

14.  Screen Wall Door Height

15.  HDMI Plate

16.  Wood Doors

17.  Preferred Security

18.  Preferred Roofer

19.  Door 4.430HB

20.  Crane location

21.  Mechanical Unit Site Delivery

22.  Auto Operator Clarification

23.  Security Cable Topology

24.  Reuse of Existing Conduit

25.  Level 3 RCP

26.  Grout vs. Silicone Sealant

27.  Project Safety

28.  DF-2 Glazing Film

29.  Healthcare Accessories

30.  Laboratory Casework

31.  Casework Demolition

32.  Alternate 1

33.  Fall Protection System

34.  Roof Warranty

35.  Low voltage cabling and Access Controls

36.  Lab Casework

37.  HVAC Spec

38.  Logistics Plan

39.  Helicopter or crane

40.  Jaggaer Portal Upload Issues

41.  Site-walk sign-in sheet

42.  access control scope

43.  access control scope

44.  access control scope

45.  access control scope

46.  access control scope

47.  access control scope

48.  access control scope

49.  Site Walk

50.  Addendum 5 (Missing?)

51.  Drawings Missing

52.  Drawings and Specs

53.  Revised Drawings Confirmation

54.  Revised CD Drawings Date

55.  Drawings

56.  Revised and Reissued Specification Sections

57.  Omitted Specification Sections

58.  Structural Drawings

59.  Addendum 5 Change Narrative

60.  RFP Due Date

61.  Alternates

62.  Re-Bid RFI Deadline

63.  Re-Bid Site Walk

64.  Sealed Bid Opening Update

65.  Question Submittal

66.  Question Submittal

67.  Floor Plans

68.  TA7 & TA9V Clarification

69.  Signage Clarification

70.  BSL-3 Cove Base Clarifications

71.  RS-1 Clarification

72.  BSL-3 Head/Jamb Detail

73.  Door Clarification at BSL-3

74.  Narrow Lite vs. Half Lite Clarification

75.  Narrow Lite vs. Half Lite Clarification

76.  Door Panel FG Clarification

77.  Owner-Requested Door Change Clarification

78.  Security Door Hardware Clarification

79.  Level 2 Door Clarification

80.  Elevation Clarification

81.  Elevation Clarification

82.  D2 Glazing Film Information

83.  Test Piece Requirement

84.  Window IN01 Jamb Details

85.  Specification Section 088000

86.  Code Requirements

87.  Raceway Clarification

88.  Device Clarification

89.  Alcove Light Fixture

90.  Column Finish Clarification

91.  Column Finish Clarification

92.  Painting Existing Corridors

93.  Sealant at Gyp Partitions

94.  Partition Width Clarification

95.  Partition Type Clarification

96.  Partition Type Clarification

97.  Delegated Design For Gyp Framing

98.  Screenwall Doorway Dimensions

99.  Fall Protection Roof Anchors

100.  Existing Slab Rebar

101.  Firestopping Requirements at Roof Slab

102.  Screenwall Column Sizing

103.  3" Overcut at Cores

104.  Louver Panel Salvage Clarification

105.  Structural Demo Clarification

106.  Roof Equipment Signed & Sealed Shops

107.  Deck Mounted Item Clarification

108.  Sealing Metal Box at BSL-3 Light Fixtures

109.  Metal Closure Plate at BSL-3

110.  Corner Bead Joint at BSL-3

111.  Sterilizers

112.  Eyewash EW2 Clarification

113.  Lab Sinks w/ Eyewash

114.  SK-4 and SK-4A

115.  Combination Shower/Eyewash

116.  Existing Lab Casework Removal

117.  Laboratory Casework Responsibility

118.  AV-1 HDMI Plate

119.  AV Cabling

120.  Data Communications Cabling

121.  O2 Sensor Location

122.  New Electrical Circuits

123.  TAB & Pre-Readings

124.  Sanitary Drip Pans

125.  Level 3 RCP

126.  Operating Room Wall Penetrations

127.  Schedule of Level 3 OR Work

128.  Crawl Space Confirmation

129.  UTSW Commissioning Plan

130.  Systems Requiring Hot Tie-Ins Clarification

131.  Panel Shutdowns

132.  HVAC System Cleaning Clarification

133.  UTSW ICRA Policies

134.  HEPA Filtered BSL-3 Exhaust

135.  Bubble Tight Dampers Confirmation

136.  Supply Duct Contamination Issue

137.  Exhaust Contamination Issue at Autoclaves

138.  BSL-3 Research

139.  Sequence of Operations, BSL-3 Decontamination

140.  BSL-3 Sequence of Operations In Exhaust Failure

141.  BSL-3 Sequence of Operations In Power Failure

142.  Sequence of Operations, Hardwire Safeties

143.  BSL-3 Shutdown Sequence of Operations

144.  BSL-3 Startup Sequence of Operations

145.  Sequence of Operations, Exhaust Interlock

146.  Missing Docs

147.  Alternates

148.  Responsibility Matix

149.  Site Walk Sign-in sheet

150.  CUH 4.219

151.  Prebid Meeting SIS

152.  EST

153.  Commissioning

# Questions & Answers

## Q1.  Outdated Part Numbers

Please confirm desired card reader and Lenel control board part numbers, specification part numbers are outdated.

Asked 8/18/2026 at 3:57 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.). The Owner will install the cabling, terminate the wires, and install the system. Answered 8/26/2026 at 9:29 AM CDT by Amanda Usrey

## Q2.  Security Device Model Numbers

Please provide desired model numbers for the “EP” emergency blue pull stations and the “DR” security door release buttons shown on plans.

Asked 8/18/2026 at 3:57 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.). The Owner will install the cabling, terminate the wires, and install the system. Answered 8/26/2026 at 9:29 AM CDT by Amanda Usrey

## Q3.  "KP" Security Keypad

For the “security keypad” KP symbol shown on the security plans, there is no specification for this symbol. Is this a card reader with integrated keypad? Please provide desired model number.

Asked 8/18/2026 at 3:57 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.). The Owner will install the cabling, terminate the wires, and install the system and devices Answered 8/26/2026 at 9:30 AM CDT by Amanda Usrey

## Q4.  Access Control Panels/Power Supplies

Is there an existing access control panel that can be used and expanded, as well as power supplies, or will new enclosures and power supplies be needed?

Asked 8/18/2026 at 3:56 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.). The Owner will install the cabling, terminate the wires, and install the system and devices Answered 8/26/2026 at 9:30 AM CDT by Amanda Usrey

## Q5.  IDF Closet Location

Where is the IDF closet located that will be used for access control doors on this project?

Asked 8/18/2026 at 3:56 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.) to the nearest accessible corridor ceiling. The Owner will install the cabling, terminate the wires, and install the system. Answered 8/26/2026 at 9:31 AM CDT by Amanda Usrey

## Q6.  Licensing for VMS

Specifications state to provide licensing for video surveillance integration with the card readers and reference the video surveillance specs, which are not provided. Is this licensing required, and if so, which VMS is in use?

Asked 8/18/2026 at 3:55 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.). The Owner will install the cabling, terminate the wires, and install the system. Answered 8/26/2026 at 9:31 AM CDT by Amanda Usrey

## Q7.  Lenel Licensing Confirmation

Specifications state to provide Lenel licensing for new reader additions (64 reader expansion) – will this be required on this project?

Asked 8/18/2026 at 3:55 PM CDT

ANSWER Not applicable. The Owner will provide all security licenses and perform all terminations. Answered 8/26/2026 at 9:31 AM CDT by Amanda Usrey

## Q8.  Panel H4CA

Please provide information (Panel brand/type and breaker type/KAIC) for Panel H4CA.

Asked 8/18/2026 at 3:53 PM CDT

ANSWER Refer to the specifications. Answered 8/26/2026 at 9:31 AM CDT by Amanda Usrey

## Q9.  Construction Schedule - Pricing & Delivery

Please confirm if the dates included on the Pricing and Delivery document will be updated in section 1.3, as the NTP date has passed.

Asked 8/18/2026 at 3:11 PM CDT

ANSWER I have added the dates to Addendum 9. Yes, the dates have changed. Answered 8/19/2026 at 9:28 AM CDT by Amanda Usrey

## Q10.  Alternates

Please confirm where the alternates should be included with pricing within the submission.

Asked 8/18/2026 at 3:06 PM CDT

ANSWER Add to the schedule of values in 2.10 Answered 8/19/2026 at 8:55 AM CDT by Amanda Usrey

## Q11.  Curtain Track

Sheet A-553/B3, notes 10 21 24a spec section. Please confirm this included in the spec book if to be provided and installed by GC.

Asked 8/18/2026 at 2:59 PM CDT

ANSWER The details is not used. Answered 8/26/2026 at 9:32 AM CDT by Amanda Usrey

## Q12.  Alternates

In spec section 01 23 00, 3 alternates are listed in this section. Can more description be provided for the base bid option for each and the specifications for the alternate products?

Asked 8/18/2026 at 2:50 PM CDT

ANSWER The contractor must demonstrate compliance with the basis of design if an alternative is proposed. Answered 8/26/2026 at 9:33 AM CDT by Amanda Usrey

## Q13.  Roof Tie Back Anchor

Sheet A-105/D1 notes spec section 11 24 26a for the safety tie back at the roof. This doesnt appear in the spec book. Please confirm who is responsible for providing and installing this scope of work and provide information for this spec.

Asked 8/18/2026 at 2:44 PM CDT

ANSWER Provide system that matches existing. Pro-Bel System or approved equal. See attached example. Answered 8/26/2026 at 9:33 AM CDT by Amanda Usrey

## Q14.  Screen Wall Door Height

Elevations 3 and 5 on sheet S-250 state to reference Architectural drawings for dimensions of doorways in the louvered screenwall system. However, the Architectural drawings provides only the width of the opening. Please specify correct dimensions for doorway openings.

Asked 8/18/2026 at 2:26 PM CDT

ANSWER 7'5" from north east corner from screening wall. Verify with panel dimensions Answered 8/26/2026 at 9:34 AM CDT by Amanda Usrey

## Q15.  HDMI Plate

Keynote 3/T-201 indicates to provide an HDMI plate and extension cable to D1 display. Please provide basis of design for AV-1 HDMI plate.

Asked 8/18/2026 at 2:10 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.) to the nearest accessible corridor ceiling. The Owner will install the cabling, terminate the wires, and install the system. Answered 8/26/2026 at 9:37 AM CDT by Amanda Usrey

## Q16.  Wood Doors

Please specify what "cut" of White Maple is required for the new wood doors. The finish schedule points out that they are to be "center-balanced/book match", but the actual cut isn't specified, which could make a difference in pricing. Please confirm whether they are to be Plain-Sliced, Rotary Cut, Quarter-Sawn, etc.

Asked 8/18/2026 at 2:10 PM CDT

ANSWER Plain Sliced to match existing doors Answered 8/26/2026 at 9:38 AM CDT by Amanda Usrey

## Q17.  Preferred Security

Please confirm if the building has a preferred or required security vendor to work with on this project.

Asked 8/18/2026 at 2:08 PM CDT

ANSWER Yes has warranty, use Supreme (Tyler Lynch -Phone 214-600-9138) Answered 8/26/2026 at 9:39 AM CDT by Amanda Usrey

## Q18.  Preferred Roofer

Please confirm if the building has a preferred roofer or one that holds a roofing warranty that is required for this project.

Asked 8/18/2026 at 2:08 PM CDT

ANSWER Please confirm if the building has a preferred roofer or one that holds a roofing warranty that is required for this project. Yes has warranty, use Supreme (Tyler Lynch -Phone 214-600-9138) Answered 8/26/2026 at 9:39 AM CDT by Amanda Usrey

## Q19.  Door 4.430HB

On the door schedule, Door 4.430HB shows to be an aluminum panel door, but the frame called for is Hollow Metal. AD Systems does not provide HM frames but only provides Aluminum frames. Please confirm that this door is to be an aluminum slider.

Asked 8/18/2026 at 2:07 PM CDT

ANSWER Yes Answered 8/26/2026 at 9:39 AM CDT by Amanda Usrey

## Q20.  Crane location

Can we get confirmation we can choose to NOT put the crane on the transit bus ramp next to the building?

Asked 8/18/2026 at 2:07 PM CDT

ANSWER Please refer to the proposed crane location indicated on the plan. The preferred option is to position the crane at the ambulance driveway. The contractor shall coordinate with the crane supplier and equipment vendor to confirm that the equipment weight is within the crane’s capacity and that the crane can safely access and operate within the proposed area. If this option is not feasible, the contractor may propose alternatives, including delivering the equipment in sections and assembling it on the roof using a smaller crane or transporting the sections via the facility elevator. All options are subject to review and approval by the applicable entities. [Attachment: Crane-Q-31-Q-50.pdf] Answered 8/26/2026 at 9:40 AM CDT by Amanda Usrey

## Q21.  Mechanical Unit Site Delivery

Can we get confirmation that it is means and methods to set the new mechanical unit, and that a helicoper is not required?

Asked 8/18/2026 at 2:06 PM CDT

ANSWER We recommend locating the crane at the Emergency Department entrance. Please refer to the attached sketch. A helicopter is not required. [Attachment: Crane-Q-31-Q-50.pdf] Answered 8/26/2026 at 9:41 AM CDT by Amanda Usrey

## Q22.  Auto Operator Clarification

Specification section 08 71 13 Automatic Door Operators lists Besam SW100 as the basis of design for auto operators. However, the hardware schedule in specification section 08 71 00 Door Hardware calls for a "Quad 4000" auto operator, which is not a Besam product. "QUAD" is not listed as an acceptable manufacturer in specification 08 71 13. Please clarify which is correct.

Asked 8/18/2026 at 2:06 PM CDT

ANSWER Quad 4000 is acceptable Answered 8/26/2026 at 9:41 AM CDT by Amanda Usrey

## Q23.  Security Cable Topology

Please provide the existing cable topology that the new security cabling should match as indicated in general note B on sheet TS-201.

Asked 8/18/2026 at 2:02 PM CDT

ANSWER Will be provided and installed by owner Answered 8/26/2026 at 9:41 AM CDT by Amanda Usrey

## Q24.  Reuse of Existing Conduit

Please confirm whether use of existing conduit is acceptable for new circuits. Previous RFI response noted that SSR takes no exception, but needs to be confirmed with UTSW if acceptable.

Asked 8/18/2026 at 2:00 PM CDT

ANSWER Existing conduit may be reused, provided it meets the specifications and applicable codes. Answered 8/26/2026 at 9:42 AM CDT by Amanda Usrey

## Q25.  Level 3 RCP

Please provide a reflected ceiling plan for Level 3 where above-ceiling plumbing work is required.

Asked 8/18/2026 at 1:57 PM CDT

ANSWER The overall Level 3 reflected ceiling plan is provided for reference only. The contractor is responsible for field verification and confirmation of existing conditions. Answered 8/26/2026 at 9:42 AM CDT by Amanda Usrey

## Q26.  Grout vs. Silicone Sealant

Details C4, C5, and D5 on sheet Q-550 indicate that caulking at the bio-seal should be done using a suitable grout or RTV. Please confirm whether 100% silicone sealant can be used at this location.

Asked 8/18/2026 at 1:56 PM CDT

ANSWER No, used specified ceiling type Answered 8/26/2026 at 9:42 AM CDT by Amanda Usrey

## Q27.  Project Safety

In spec section 01 35 23 - Project Safety Requirements, can you confirm if the qualified person that is requested for the anticipated budget of $600,000 (2.1.3 notes PSA-IT), can be the same individual as the Superintendent? For this project, is this person required onsite full time, or as needed?

Asked 8/18/2026 at 1:54 PM CDT

ANSWER Has to be separate person Answered 8/26/2026 at 9:43 AM CDT by Amanda Usrey

## Q28.  DF-2 Glazing Film

Please provide a basis of design for DF-2 glazing film shown in the finish schedule.

Asked 8/18/2026 at 1:52 PM CDT

ANSWER Refer to the specifications. Answered 8/26/2026 at 9:43 AM CDT by Amanda Usrey

## Q29.  Healthcare Accessories

Please provide a basis of design for all heathcare accessories that are to be provided and installed by Contractor. Specification Section 10 28 13 states to refer to schedule on Drawings, but the Drawings do not provide a schedule.

Asked 8/18/2026 at 1:51 PM CDT

ANSWER Accessories will be provided by the Owner unless specifically noted as contractor-provided. Answered 8/26/2026 at 9:44 AM CDT by Amanda Usrey

## Q30.  Laboratory Casework

Please confirm definitively whether laboratory casework, laboratory sinks, laboratory accessories, and laboratory service fixtures are by Owner, or if they should be part of Contractor's proposal.

Asked 8/18/2026 at 1:47 PM CDT

ANSWER Casework will be provided by the Owner. The contractor is responsible for all utility connections. Answered 8/26/2026 at 9:44 AM CDT by Amanda Usrey

## Q31.  Casework Demolition

Sheet A-104: Please clarify whether the casework islands in AP Histology 41039 are to be removed and salvaged by Contractor or by Owner.

Asked 8/18/2026 at 1:45 PM CDT

ANSWER The contractor shall remove and salvage all casework, except for items identified by the Owner during the post-award site walk. Answered 8/26/2026 at 9:44 AM CDT by Amanda Usrey

## Q32.  Alternate 1

Alternate 1 indicates to provide a removable wall panel system at the existing storefront wall chase, however, no additional information or specifications for this system have been provided. Please provide a basis of design and installation requirements. Additionally, please confirm that this system is acceptable for use within the BSL-3 containment barrier and provide any requirements necessary to maintain a flush, continuous, and sealed surface.

Asked 8/18/2026 at 1:42 PM CDT

ANSWER Bases of design is Bio CR-3 by Lifescience INC or approved equal Answered 8/26/2026 at 9:44 AM CDT by Amanda Usrey

## Q33.  Fall Protection System

Per the previously answered RFI, please confirm UTSW's preferred fall protection system for this project. Also, please provide specification section 11 24 26 for reference as indicated in detail D1/A-105.

Asked 8/18/2026 at 1:30 PM CDT

ANSWER Provide system that matches existing. Pro-Bel System or approved equal. See attached example. Answered 8/26/2026 at 9:45 AM CDT by Amanda Usrey

## Q34.  Roof Warranty

Please provide if the roof is still under warranty. also please provide the roof contractor who is maintaining it currently,

Asked 8/18/2026 at 8:11 AM CDT

ANSWER Yes has warranty, use Supreme (Tyler Lynch -Phone 214-600-9138) Answered 8/26/2026 at 9:45 AM CDT by Amanda Usrey

## Q35.  Low voltage cabling and Access Controls

Please confirm low voltage cabling and access controls including card readers are by Owner

Asked 8/18/2026 at 8:11 AM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.) to the nearest accessible corridor ceiling. The Owner will install the cabling, terminate the wires, and install the system. Answered 8/26/2026 at 9:46 AM CDT by Amanda Usrey

## Q36.  Lab Casework

Please confirm that the lab casework is by owner.

Asked 8/18/2026 at 8:10 AM CDT

ANSWER Casework will be provided by the Owner. The contractor is responsible for all utility connections. Answered 8/26/2026 at 9:46 AM CDT by Amanda Usrey

## Q37.  HVAC Spec

As per the prebid meeting it was mentioned that the HVAC Units are open specs and any manufacturer can be used as long as it meets the criteria. Please confirm

Asked 8/18/2026 at 8:09 AM CDT

ANSWER Confirmed. Has to be approved equal Answered 8/26/2026 at 9:46 AM CDT by Amanda Usrey

## Q38.  Logistics Plan

Can you please provide a logistics plan for the crane if acceptable.

Asked 8/18/2026 at 8:08 AM CDT

ANSWER A draft crane plan is provided for reference only. The GC is responsible for developing the crane logistics plan and submitting it for approval. Answered 8/26/2026 at 9:46 AM CDT by Amanda Usrey

## Q39.  Helicopter or crane

Can a helicopter or a big crane be used to bring up the HVAC unit or the screen wall to the roof? Please advise

Asked 8/18/2026 at 8:07 AM CDT

ANSWER Please refer to the proposed crane location indicated on the plan. The preferred option is to position the crane at the ambulance driveway. The contractor shall coordinate with the crane supplier and equipment vendor to confirm that the equipment weight is within the crane’s capacity and that the crane can safely access and operate within the proposed area. If this option is not feasible, the contractor may propose alternatives, including delivering the equipment in sections and assembling it on the roof using a smaller crane or transporting the sections via the facility elevator. All options are subject to review and approval by the applicable entities. [Attachment: Crane-Q-31-Q-50.pdf] Answered 8/26/2026 at 9:47 AM CDT by Amanda Usrey

## Q40.  Jaggaer Portal Upload Issues

The portal does not let us upload any attachments. When we try to click upload it denies it. Please help resolve this issue.

Asked 8/18/2026 at 8:06 AM CDT

ANSWER Will you please send me a screen shot of what you are seeing on your end? Answered 8/19/2026 at 9:39 AM CDT by Amanda Usrey

## Q41.  Site-walk sign-in sheet

Where do I find it, please...Thanks!

Asked 8/17/2026 at 2:55 PM CDT

ANSWER The 10th attachment under pre-requisites Answered 8/19/2026 at 9:06 AM CDT by Amanda Usrey

## Q42.  access control scope

Please confirm desired card reader and Lenel control board part numbers, specification part numbers are outdated

Asked 8/12/2026 at 3:32 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.). The Owner will install the cabling, terminate the wires, and install the system. Answered 8/26/2026 at 11:47 AM CDT by Amanda Usrey

## Q43.  access control scope

Please provide desired model numbers for the “EP” emergency blue pull stations and the “DR” security door release buttons shown on plans

Asked 8/12/2026 at 3:32 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.). The Owner will install the cabling, terminate the wires, and install the system. Answered 8/26/2026 at 11:47 AM CDT by Amanda Usrey

## Q44.  access control scope

For the “security keypad” KP symbol shown on the security plans, there is no specification for this symbol. Is this a card reader with integrated keypad? Please provide desired model number.

Asked 8/12/2026 at 3:31 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.). The Owner will install the cabling, terminate the wires, and install the system and devices Answered 8/26/2026 at 11:46 AM CDT by Amanda Usrey

## Q45.  access control scope

Is there an existing access control panel that can be used and expanded, as well as power supplies, or will new enclosures and power supplies be needed?

Asked 8/12/2026 at 3:31 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.). The Owner will install the cabling, terminate the wires, and install the system and devices Answered 8/26/2026 at 11:46 AM CDT by Amanda Usrey

## Q46.  access control scope

Where is the IDF closet located that will be used for access control doors on this project?

Asked 8/12/2026 at 3:31 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.) to the nearest accessible corridor ceiling. The Owner will install the cabling, terminate the wires, and install the system. Answered 8/26/2026 at 11:46 AM CDT by Amanda Usrey

## Q47.  access control scope

Specifications state to provide licensing for video surveillance integration with the card readers and reference the video surveillance specs, which are not provided. Is this licensing required, and if so, which VMS is in use?

Asked 8/12/2026 at 3:30 PM CDT

ANSWER The contractor is responsible for providing raceways (conduit, wall boxes, etc.). The Owner will install the cabling, terminate the wires, and install the system. Answered 8/26/2026 at 11:45 AM CDT by Amanda Usrey

## Q48.  access control scope

1. Specifications state to provide Lenel licensing for new reader additions (64 reader expansion) – will this be required on this project?

Asked 8/12/2026 at 3:30 PM CDT

ANSWER Not applicable. The Owner will provide all security licenses and perform all terminations. Answered 8/26/2026 at 11:45 AM CDT by Amanda Usrey

## Q49.  Site Walk

Will there be another site walk since this has opened back up to bid?

Asked 8/12/2026 at 2:54 PM CDT

ANSWER The pre-bid and site walk was labeled in addendum 5 Answered 8/12/2026 at 4:06 PM CDT by Amanda Usrey

## Q50.  Addendum 5 (Missing?)

When downloaded, download shows as Addendum 6, not 5.

Asked 8/11/2026 at 12:27 PM CDT

ANSWER Sorry, that was a typo on my part. That is Addendum 5 Answered 8/11/2026 at 2:31 PM CDT by Amanda Usrey

## Q51.  Drawings Missing

Sheet S001, S002, S003 are missing in the plan set. Please confirm that these have been removed,

Asked 8/11/2026 at 10:12 AM CDT

ANSWER Revised drawings and specifications are now attached in the pre-requisites Answered 8/12/2026 at 4:07 PM CDT by Amanda Usrey

## Q52.  Drawings and Specs

Please confirm that the new drawings and specifications added to the portal supersede the previously issued drawings and specifications.

Asked 8/11/2026 at 10:07 AM CDT

ANSWER Revised drawings and specifications are now attached in the pre-requisites Answered 8/12/2026 at 4:07 PM CDT by Amanda Usrey

## Q53.  Revised Drawings Confirmation

Please confirm the revised set of drawings issued 8/6/2026 as part of Addendum 5 re-opening of the RFP are the contract documents, and any revisions associated with Addendums #1-4 from the original RFP are null.

Asked 8/10/2026 at 2:34 PM CDT

ANSWER Revised drawings and specifications are now attached in the pre-requisites Answered 8/12/2026 at 4:07 PM CDT by Amanda Usrey

## Q54.  Revised CD Drawings Date

Addendum 5 issued on 8/6/2026 to Jaggaer indicates the revised CD drawings and specifications issued should be dated 7/28/2026; however, the actual files are drawings dated 12/13/2024. The addendum callouts on the revised plans reference Add#1 dated 12/13/2024 and 10/21/2024. Please confirm this is the correct set of drawings.

Asked 8/10/2026 at 2:33 PM CDT

ANSWER Revised drawings and specifications are now attached in the pre-requisites Answered 8/12/2026 at 4:07 PM CDT by Amanda Usrey

## Q55.  Drawings

The current drawings show a date of 12/13/2024. The previous drawings that we bid from looks like we were bidding MEP from drawings dated 3/13/2026. Do we ask for pricing based off the current released drawings? Or the previous addendum 1 drawings?

Asked 8/10/2026 at 10:10 AM CDT

ANSWER Revised drawings and specifications are now attached in the pre-requisites Answered 8/12/2026 at 4:08 PM CDT by Amanda Usrey

## Q56.  Revised and Reissued Specification Sections

Several retained specification sections contain substantive revisions that may affect pricing. Please provide a concise change narrative identifying revisions to scope, products, performance requirements, testing, coordination, commissioning, warranties, and closeout requirements.

Asked 8/6/2026 at 2:18 PM CDT

ANSWER Revised drawings and specifications are now attached in the pre-requisites Answered 8/12/2026 at 4:09 PM CDT by Amanda Usrey

## Q57.  Omitted Specification Sections

The following previously issued sections are omitted from the revised Project Manual: 01 31 26; 01 77 01; 01 78 36; 02 41 00; 08 34 23; 08 41 13; 11 70 00; 26 00 00; 26 24 17; 26 27 26; 26 28 13; 26 28 16; 26 29 20; 26 29 23; 26 41 13; 26 51 00; and 28 31 00. Please confirm whether these sections and their associated scope were deleted, replaced, consolidated into other sections, or remain applicable. Specifically identify the controlling requirements for demolition, cleanroom windows, storefront/glazing, laboratory equipment, electrical systems, and fire-alarm modifications.

Asked 8/6/2026 at 2:17 PM CDT

ANSWER Revised drawings and specifications are now attached in the pre-requisites Answered 8/12/2026 at 4:09 PM CDT by Amanda Usrey

## Q58.  Structural Drawings

Revised Drawing Index G-001 continues to list S001, S002, and S003, but these sheets are not included in the revised package. S200 and S511 also reference S002. Please confirm that the previously issued S001, S002, and S003 remain applicable without revision, or provide revised sheets.

Asked 8/6/2026 at 2:16 PM CDT

ANSWER Revised drawings and specifications are now attached in the pre-requisites Answered 8/12/2026 at 4:09 PM CDT by Amanda Usrey

## Q59.  Addendum 5 Change Narrative

Please provide a concise narrative identifying all substantive scope changes incorporated into the revised drawings and specifications since the previous bid issue, including work added, deleted, relocated, or modified.

Asked 8/6/2026 at 2:15 PM CDT

ANSWER Revised drawings and specifications are now attached in the pre-requisites Answered 8/12/2026 at 4:09 PM CDT by Amanda Usrey

## Q60.  RFP Due Date

Addendum 5 currently shows the RFP due date as Monday, September 7, 2026, which is a holiday (Labor Day) when offices are closed. Can the RFP due date be changed to Friday, September 4, 2026?

Asked 8/6/2026 at 12:13 PM CDT

ANSWER RFP has been updated Answered 8/11/2026 at 2:36 PM CDT by Amanda Usrey

## Q61.  Alternates

Do any of the alternates from the previous release of this project still apply? Or have they all been removed from this project?

Asked 8/6/2026 at 9:55 AM CDT

ANSWER This is a new package. The contractor shall price it without considering the previous package. Answered 8/26/2026 at 11:45 AM CDT by Amanda Usrey

## Q62.  Re-Bid RFI Deadline

The summary sheet notes the RFI deadline as August 6th, 2026, at 4:00 pm. Since this RFP was just reopened today, August 6th, with updated drawings and specifications issued, can the RFI deadline be extended?

Asked 8/6/2026 at 8:34 AM CDT

ANSWER Yes Answered 8/6/2026 at 9:40 PM CDT by Marcus Howard

## Q63.  Re-Bid Site Walk

Since this RFP has opened up for re-bid today, will there be another pre-bid conference and site walk scheduled? If so, please provide information.

Asked 8/6/2026 at 8:31 AM CDT

ANSWER Yes, information will be provided shortly. Answered 8/6/2026 at 9:39 PM CDT by Marcus Howard

## Q64.  Sealed Bid Opening Update

Please see the attached document for the Sealed Bid Opening, scheduled for 5/18/2026 at 12:30PM CST.

Asked 5/16/2026 at 8:09 PM CDT

ANSWER Please see the attached document for the Sealed Bid Opening, scheduled for 5/18/2026 at 12:30PM CST. [Attachment: RFP Sealed Proposal - CUH 4.219 Microbiology Lab Expansion Phase II (BSL-3) 5.18.26.pdf] Answered 5/16/2026 at 8:09 PM CDT by Marcus Howard

## Q65.  Question Submittal

Note #16 on drawing P-111 states that the gas manifold MGM-1 is provided by the Owner, but this manifold is scheduled on drawing P-000 implying it is contractor furnished. Who is responsible for furnishing this manifold?

Asked 4/30/2026 at 2:18 PM CDT

ANSWER Manifold provided by contractor. Cylinders provided by owner. Answered 4/30/2026 at 2:18 PM CDT by Marcus Howard

## Q66.  Question Submittal

Drawing MP-204.1 appears to show the MPC line running down corridor 04.C44 adjacent to the steam line terminating on the 3rd floor. Is the intent that that his MPC line be routed in the ceiling of the 3rd floor and not the 4th floor?

Asked 4/30/2026 at 2:16 PM CDT

ANSWER No. Should run in 4th floor ceiling. Answered 4/30/2026 at 2:16 PM CDT by Marcus Howard

## Q67.  Floor Plans

Please provide floor plans for Levels 01, 02, 03, and 04.

Asked 4/15/2026 at 3:32 PM CDT

ANSWER UTSW to provide. Answered 5/6/2026 at 4:13 PM CDT by Marcus Howard

## Q68.  TA7 & TA9V Clarification

Floor Plan B2/A-104 and Elevation C2/A-553 indicate TA7 (assumed paper towel dispenser), and TA9V (assumed soap dispenser). However, there is no corresponding schedule provided in the plans, nor any associated specification. Please confirm what is represented and if these items are to be OFOI. Additionally, please provide a responsibility matrix for these and any similar items.

Asked 4/15/2026 at 3:31 PM CDT

ANSWER Refer to G-001 for mounting diagram and associated TA items. Refer to 10 28 13 for additional information on fabrication and product selections. Revised specifications to include BOD for each fixture to be provided. Answered 5/6/2026 at 4:13 PM CDT by Marcus Howard

## Q69.  Signage Clarification

Specification Section 101400 for signage is provided, but no signage is indicated on the documents. Please confirm whether signage is to be provided by Contractor and, if so, please provide signage schedule and details.

Asked 4/15/2026 at 3:31 PM CDT

ANSWER UTSW to confirm. Answered 5/6/2026 at 4:10 PM CDT by Marcus Howard

## Q70.  BSL-3 Cove Base Clarifications

Please clarify the necessary details for the resinous flooring cove base in the BSL-3 (AFB Lab) and the standard lab area. Are the base details different to meet BSL-3 requirements? A3/I001 calls for resinous flooring cove base with seamless epoxy flooring (assumed to be RF-1) with a top edge labeled FT-5 and reference to Specification Section 093050e. However, FT-5 and Specification Section 093050e are not provided in the drawings or specs. B2/Q550 shows a BSL-3 integral cove base detail; however, the detail references vinyl flooring that is not reflected in the finish schedule. Please advise. 78. Specification Section 101400 for signage is provided, but no signage is indicated on the documents. Please confirm whether signage is to be provided by Contractor and, if so, please provide signage schedule and details.

Asked 4/15/2026 at 3:31 PM CDT

ANSWER Details to be updated. Trim for epoxy flooring is recommended by the epoxy manufacturer. Answered 5/6/2026 at 4:05 PM CDT by Marcus Howard

## Q71.  RS-1 Clarification

Elevations C1 and C2 on sheet A-553 call out RS-1 at the wall base. RS-1 was not provided in the Finish Legend on sheet I-001. Please advise.

Asked 4/15/2026 at 3:30 PM CDT

ANSWER Finish outdated, refer to I-001 for finish designations. Will be updated in future drawing issuance. Answered 5/6/2026 at 4:05 PM CDT by Marcus Howard

## Q72.  BSL-3 Head/Jamb Detail

Detail C3/A-551 shows a BSL-3 head/jamb detail. This detail is not mentioned anywhere else in the drawings. Please confirm if doors 4.430J, 4.430L, and 4.430HB within the BSL-3 containment barrier are to receive this detail.

Asked 4/15/2026 at 3:30 PM CDT

ANSWER All doors within BSL-3 containment are to be utilize the detail provided. Answered 5/6/2026 at 4:04 PM CDT by Marcus Howard

## Q73.  Door Clarification at BSL-3

The Door and Frame Schedule on sheet A-551 calls for door 4.430L at Ante Rm entry to receive one (1) rubber seal at bottom of door, and door 4.430J at AFB Lab entry to receive one (1) adjustable gasket at bottom of door. Please review door, frame, and hardware requirements for these spaces and confirm these openings are acceptable, or advise if any additional hardware is required.

Asked 4/15/2026 at 3:29 PM CDT

ANSWER Rubber seal and and adjustable gaskets may need to be removed. HDR to confirm with SSR based on negative pressurization requirements for BSL-3 Function. Answered 5/6/2026 at 3:20 PM CDT by Marcus Howard

## Q74.  Narrow Lite vs. Half Lite Clarification

Floor Plan B2/A-104 appears to show door 4.430J to have a half glass lite; however, the Door and Frame Schedule on sheet A-551 calls for a narrow lite. Please confirm which is correct.

Asked 4/15/2026 at 3:29 PM CDT

ANSWER Door is to be HG type, will be updated. Answered 5/6/2026 at 3:56 PM CDT by Marcus Howard

## Q75.  Narrow Lite vs. Half Lite Clarification

The Door and Frame Schedule on sheet A-551 calls for a narrow lite at door 4.430L; however, elevation C2/A-553 shows a half glass door. Please confirm which is correct.

Asked 4/15/2026 at 3:29 PM CDT

ANSWER Door is to be HG type, will be updated. Answered 5/6/2026 at 3:18 PM CDT by Marcus Howard

## Q76.  Door Panel FG Clarification

The Door and Frame Schedule on sheet A-551 references door 4.430N having panel type FG. There is no FG panel shown on the interior panel legend. Please confirm the panel type of this door.

Asked 4/15/2026 at 3:28 PM CDT

ANSWER FG equates to HG, designation to be updated. Answered 5/6/2026 at 3:21 PM CDT by Marcus Howard

## Q77.  Owner-Requested Door Change Clarification

B2/A-104 notes that there is an Owner-requested change to substitute door 4.430W for a sliding door. Please confirm whether this door is to copy 4.430HB or 4.430N, and clarify which hardware set this door is to receive.

Asked 4/15/2026 at 3:28 PM CDT

ANSWER Door will not be sliding. Disregard Note, will be updated in forthcoming Addendum. Answered 8/6/2026 at 8:29 AM CDT by Marcus Howard

## Q78.  Security Door Hardware Clarification

The Door and Frame Schedule on sheet A-551 references door 4.430G receiving hardware set C201GPW. Per the hardware schedule, this door receives a card reader and electric components that are not shown on TS-201. Please confirm hardware requirements for door 4.430G.

Asked 4/15/2026 at 3:27 PM CDT

ANSWER SSR: The door's card reader was removed during a review for addendum 1 issue. Aprox 3-9-2026. Card reader is to remain removed, and hardware set is to be adjusting accordingly. Answered 8/6/2026 at 8:52 PM CDT by Marcus Howard

## Q79.  Level 2 Door Clarification

The Door and Frame Schedule on sheet A-551 references level 02 door 4.430K-EE. This door is not shown anywhere else on the drawings. Please confirm if this door is to be included, and what hardware is associated with this door.

Asked 4/15/2026 at 3:27 PM CDT

ANSWER Door is to not be considered and has since been removed. Answered 8/6/2026 at 8:53 PM CDT by Marcus Howard

## Q80.  Elevation Clarification

Please advise what is represented by the rectangle above the door in elevation C2/A-553.

Asked 4/15/2026 at 3:27 PM CDT

ANSWER Refer to mechanical. Answered 5/6/2026 at 3:16 PM CDT by Marcus Howard

## Q81.  Elevation Clarification

Please advise what is represented by the two (2) rectangles above the Alternate 003 window in elevation D1/A-522.

Asked 4/15/2026 at 3:26 PM CDT

ANSWER Refer to mechanical. Answered 5/6/2026 at 3:17 PM CDT by Marcus Howard

## Q82.  D2 Glazing Film Information

Please provide the Series/Style information for D2 Glazing Surface Film schedule on sheet I-001.

Asked 4/15/2026 at 3:26 PM CDT

ANSWER Series and style have not been determined at this time UTSW to advise if a product needs to be selected. Answered 5/6/2026 at 3:15 PM CDT by Marcus Howard

## Q83.  Test Piece Requirement

Specification Section 083423 calls to provide a 3'x7' test piece. Please confirm this is required.

Asked 4/15/2026 at 3:25 PM CDT

ANSWER Not required, confirm with manufacturer criteria specified and required by BSL-3 commissioning can be met. Answered 5/6/2026 at 3:14 PM CDT by Marcus Howard

## Q84.  Window IN01 Jamb Details

Window Schedule on sheet A-551 shows window IN01. There are no details for the jambs at this window. Please provide window IN01 jamb details.

Asked 4/15/2026 at 3:25 PM CDT

ANSWER IN01 is synonymous with IW01, tag will be updated to align accordingly. Answered 5/6/2026 at 3:13 PM CDT by Marcus Howard

## Q85.  Specification Section 088000

Section 088000 is missing from the Specifications. Please provide.

Asked 4/15/2026 at 3:25 PM CDT

ANSWER Refer to procurement portal, specifications have since been provided and will be issued in a future addenum. Answered 5/6/2026 at 3:12 PM CDT by Marcus Howard

## Q86.  Code Requirements

Specification Section 014100, Part 1.1-C indicates code requirements that do not coincide with those listed on sheet G-010. Please confirm which is correct, and update document to agree. Please review all other codes listed in this Section.

Asked 4/15/2026 at 3:24 PM CDT

ANSWER UTSW to clarify applicable codes, against buildint master specifications. Answered 5/6/2026 at 3:11 PM CDT by Marcus Howard

## Q87.  Raceway Clarification

Elevation C1 on sheet A-553 shows a third raceway above the typical double that is shown on all other elevations and electrical drawings. Additionally, it is not shown on corresponding elevation D4/Q-210. Please advise what this third raceway is intended for and if it is required.

Asked 4/15/2026 at 3:24 PM CDT

ANSWER Disregard, refer to MEP drawings for raceway count. Mounting height to be coordinated with mounting height requirements prio to installation. Answered 5/6/2026 at 3:07 PM CDT by Marcus Howard

## Q88.  Device Clarification

Elevations C1 & C2 on sheet A-553 show multiple devices on the wall that appear to be thermostats. Please advise what these devices are.

Asked 4/15/2026 at 3:24 PM CDT

ANSWER Refer to MEP plans for associated wall fixtures. Answered 5/6/2026 at 3:06 PM CDT by Marcus Howard

## Q89.  Alcove Light Fixture

Ceiling Plan B1/A-104 shows a can light at Alcove 4.430X that is missing on Electrical Lighting Plan A5/EL-111. Please confirm whether this can light is required at this location.

Asked 4/15/2026 at 3:23 PM CDT

ANSWER Light is required, fixture has been added in Addendum 01 Answered 5/6/2026 at 3:05 PM CDT by Marcus Howard

## Q90.  Column Finish Clarification

Floor Plan B2/A-104: Please confirm existing column at gridline M/8 is to have three (3) unfinished sides.

Asked 4/15/2026 at 3:23 PM CDT

ANSWER Incorrect, existing column is furred out and is to be refinished to achieve a uniform finish with adjacent walls. Answered 5/6/2026 at 3:03 PM CDT by Marcus Howard

## Q91.  Column Finish Clarification

Floor Plan B2/A-104: Please confirm existing column at gridline M/9 is to have four (4) unfinished sides.

Asked 4/15/2026 at 3:22 PM CDT

ANSWER Incorrect, existing column is furred out and is to be refinished to achieve a uniform finish with adjacent walls. Answered 5/6/2026 at 3:04 PM CDT by Marcus Howard

## Q92.  Painting Existing Corridors

Where drywall patching is required at existing corridors below ceiling, please confirm repainting walls is necessary from corner to corner to achieve a uniform finish with existing.

Asked 4/15/2026 at 3:22 PM CDT

ANSWER Correct, unless directed otherwise by UTSW Answered 5/6/2026 at 2:57 PM CDT by Marcus Howard

## Q93.  Sealant at Gyp Partitions

Sheet A-720 Standard Partition Types calls out "sealant" with reference to Specification Section 07 92 16a. After review of the specifications, this section does not exist. Please advise.

Asked 4/15/2026 at 3:22 PM CDT

ANSWER Refer to interior Joint sealant specifications 07 92 00, note will be updated. Answered 5/6/2026 at 2:54 PM CDT by Marcus Howard

## Q94.  Partition Width Clarification

Partition Type A on sheet A-720 notes the partition width for Mark A4 partitions as "<varies>". Please clarify.

Asked 4/15/2026 at 3:21 PM CDT

ANSWER Will be corrected in a future drawing issuance. 4" Stud with associated GWB on either side. Answered 5/6/2026 at 2:52 PM CDT by Marcus Howard

## Q95.  Partition Type Clarification

Please confirm that the wall encasing door 4.430J is partition type A4.

Asked 4/15/2026 at 3:21 PM CDT

ANSWER Correct. Answered 5/6/2026 at 2:41 PM CDT by Marcus Howard

## Q96.  Partition Type Clarification

Please provide partition type at north walls of Ante Rm 4.430L.

Asked 4/15/2026 at 3:21 PM CDT

ANSWER A4 Answered 5/6/2026 at 2:50 PM CDT by Marcus Howard

## Q97.  Delegated Design For Gyp Framing

Per Specification Section 092216, Part 1.3K, please confirm non-structural metal framing and gyp wall systems are delegated design. This is typical at BSL-3 areas to accommodate negative pressure within the lab.

Asked 4/15/2026 at 3:20 PM CDT

ANSWER This is correct, and the delegated design and associated engineering is to be provided under the contractor's scope of work and submitted to the AE team for review. Answered 5/5/2026 at 3:56 PM CDT by Marcus Howard

## Q98.  Screenwall Doorway Dimensions

Elevations 3 and 5 on sheet S-250 state to reference Architectural drawings for dimensions of doorways in the louvered screenwall system. However, the Architectural drawings do not provide any information. Please specify correct dimensions for doorway openings at these locations.

Asked 4/15/2026 at 3:19 PM CDT

ANSWER Architectural plan provides opening size, what do we need clarity on? Answered 8/6/2026 at 8:53 PM CDT by Marcus Howard

## Q99.  Fall Protection Roof Anchors

Please confirm if post-installed fall protection anchors shown in details 15/S511 and D1/A-105 are to be included in Contractors scope of work. If so, please provide specifications indicating delegated design requirements.

Asked 4/15/2026 at 3:19 PM CDT

ANSWER These should be included with contractor's scope of work. Defer to the owner of what system they want to use. UTSW to email. Answered 8/6/2026 at 8:53 PM CDT by Marcus Howard

## Q100.  Existing Slab Rebar

Please specify whether the existing concrete slab is Post-Tension or conventional rebar.

Asked 4/15/2026 at 3:18 PM CDT

ANSWER Conventional mild reinforced slab and beam system. Answered 8/6/2026 at 8:54 PM CDT by Marcus Howard

## Q101.  Firestopping Requirements at Roof Slab

Details 1/S-511 and D4/A-105 indicate firestopping at steel column penetrations in the roof slab. Please provide more information on the firestopping requirements at these locations.

Asked 4/15/2026 at 3:18 PM CDT

ANSWER Fire Stopping requirements are provided throughout Division 07 84 00 fire stopping. Refer to Construction Types for Rating Requirements at Roof line. Answered 8/6/2026 at 8:55 PM CDT by Marcus Howard

## Q102.  Screenwall Column Sizing

Details 7 & 8 on sheet S511 note HSS screenwall columns sizing per plan. However, the plans do not call out the size of HSS screenwall columns. Section 1/S511 is the only place where sizing is provided, which is a thinner wall (5/16) than horizontal supports (3/8) below slab. Please confirm requirements.

Asked 4/15/2026 at 3:18 PM CDT

ANSWER S200 indicates that screenwall post sizes are shown on elevations. Sheet S250 shows screenwall elevations with column sizes shown. Answered 8/6/2026 at 8:55 PM CDT by Marcus Howard

## Q103.  3" Overcut at Cores

Plan Note 4 on 2/S200 implies 3" overcut at cores to achieve the specified 1-1/2" minimum bar cover at all reinforcement. Please confirm this is required.

Asked 4/15/2026 at 3:17 PM CDT

ANSWER No overcut required. This note is provided to indicate core minimum clearances from existing framing and existing reinforcement. Answered 8/6/2026 at 8:55 PM CDT by Marcus Howard

## Q104.  Louver Panel Salvage Clarification

Elevation 2/SD250 indicates to remove and retain existing channel girt for reuse in final layout. Are existing louver panels to be salvaged for reuse considering new will abut existing at some point?

Asked 4/15/2026 at 3:17 PM CDT

ANSWER HDR takes no exceptions fo salvaging and re-use. All cut material is to be ground and cut to provide like-new appearance to materials that are modified as required for new screen wall system. Answered 8/6/2026 at 8:56 PM CDT by Marcus Howard

## Q105.  Structural Demo Clarification

On sheet SD200, please clarify intent of hatched lines between column lines 9 & 10. This appears to be demolition scope but is not called out or identified, and no new work is shown on sheet S200.

Asked 4/15/2026 at 3:16 PM CDT

ANSWER This is not intended to be demolition scope. No work at these locations. Answered 8/6/2026 at 8:59 PM CDT by Marcus Howard

## Q106.  Roof Equipment Signed & Sealed Shops

Sheet S-001, Part I, Note M1 states that all roof top equipment curbs, roof top mechanical equipment, equipment tie downs, and connections of all equipment to building structure are to be designed and engineered by a registered Specialty Engineer retained by the mechanical equipment supplier. Are Signed and Sealed shop drawings and calculations to be submitted? Please confirm this is required.

Asked 4/15/2026 at 3:16 PM CDT

ANSWER Per S001, Part XII Section B.2.a - Roof Top Equipment and Anchorages (S&S) should be submitted. As stated in this section (S&S) indicates that shop drawings and deldgated design submittals shall be sealed per the project specifications by an engineer registered in the state where the project is located. Answered 8/6/2026 at 9:01 PM CDT by Marcus Howard

## Q107.  Deck Mounted Item Clarification

Elevations C4 and D4 on sheet Q-210 show an item deck mounted near the sink fixture that is not called out. The sinks at these locations are not states to receive an eyewash. Please clarify what the item in the elevations is intended to represent.

Asked 4/15/2026 at 3:15 PM CDT

ANSWER Fixture is to be DI / RO water fixture. I.E. tied to the AquaTAP alternative. Refer to Laboratory sink schedule for clarification. Answered 5/5/2026 at 3:51 PM CDT by Marcus Howard

## Q108.  Sealing Metal Box at BSL-3 Light Fixtures

Detail A5/Q-550 notes to seal the cast metal box to ceiling at BSL-3 light fixtures. Please confirm whether 100% silicone sealant is acceptable at this location.

Asked 4/15/2026 at 3:15 PM CDT

ANSWER Correct Answered 5/5/2026 at 3:49 PM CDT by Marcus Howard

## Q109.  Metal Closure Plate at BSL-3

Detail A3/Q-550 references a metal closure plate at BSL-3 mechanical penetrations. Please specify what type of metal plate (e.g. stainless steel) is required at these locations.

Asked 4/15/2026 at 3:14 PM CDT

ANSWER Exposed metal is to be non-porous. Answered 5/5/2026 at 3:44 PM CDT by Marcus Howard

## Q110.  Corner Bead Joint at BSL-3

Please confirm whether the corner bead joint shown on B4/Q-550 at the wall to ceiling transition is acceptable prior to the application of epoxy paint.

Asked 4/15/2026 at 3:14 PM CDT

ANSWER Unless directed otherwise by epoxy manufacturer, corner bead is to be installed as per the detail. Answered 5/5/2026 at 3:43 PM CDT by Marcus Howard

## Q111.  Sterilizers

Please confirm sterilizers are to be OFCI.

Asked 4/15/2026 at 3:13 PM CDT

ANSWER Understood equipment is to be OFCI. Answered 8/6/2026 at 9:01 PM CDT by Marcus Howard

## Q112.  Eyewash EW2 Clarification

Laboratory Fixture & Fittings Schedule on sheet Q-001 lists eyewash EW2 that is not shown on the plans. The only deck mounted eyewash is at single SK-4A locations. Please confirm this meets with intent.

Asked 4/15/2026 at 3:13 PM CDT

ANSWER This is in alignment with the design intent. Answered 5/5/2026 at 3:41 PM CDT by Marcus Howard

## Q113.  Lab Sinks w/ Eyewash

Plumbing Fixture Connection Schedule on sheet P-000 notes both P-25 and P-25A sinks to have eyewash mounted on backsplash; however, only fixture P-25A provides an emergency fixture model. Additionally, corresponding fixture SK-4 on sheet Q-001 does not indicate an eyewash. Please confirm only fixture P-25A is to include eyewash, and the "eyewash" indicated for fixture P-25 is an error.

Asked 4/15/2026 at 3:13 PM CDT

ANSWER SSR: HDR to confirm which sinks are clean sinks that require the eye wash. SSR will update the fixture schedule/plans accordingly. Answered 8/6/2026 at 9:02 PM CDT by Marcus Howard

## Q114.  SK-4 and SK-4A

Please confirm SK-4 and SK-4A are to be furnished and installed by Div 22 contractor, and not Owner/Vendor as indicated in the Laboratory Sink Schedule on sheet Q-001. See fixtures P25 and P25A at Connection Schedule on sheet P-000, and sheet P-111 for corresponding locations.

Asked 4/15/2026 at 3:12 PM CDT

ANSWER Correct, annotation to be updated. Answered 5/5/2026 at 3:39 PM CDT by Marcus Howard

## Q115.  Combination Shower/Eyewash

Please confirm whether the combination safety shower/eyewash is to be provided by Owner, and Contractor is only responsible for final connections. Laboratory drawings appear to show this item to be included as Owner-provided laboratory service fixtures, however, sheet P-000 lists the combination shower/eyewash under the Plumbing Fixture Schedule.

Asked 4/15/2026 at 3:12 PM CDT

ANSWER SSR: HDR to confirm who is specifying the Safety Shower. SSR can update our fixture schdule to connection only if equipment is calling for the shower. Answered 8/6/2026 at 9:03 PM CDT by Marcus Howard

## Q116.  Existing Lab Casework Removal

Keyed note AD-01 on sheet A-104 notes to salvage existing laboratory casework and equipment, if not removed already. Please confirm Contractor is to remove and salvage the existing laboratory casework and equipment. Additionally, sheet ED-112 does not indicate any electrical demolition at these locations. Please confirm Contractor will need to make-safe and demo electrical within this lab casework.

Asked 4/15/2026 at 3:11 PM CDT

ANSWER Contractor will need to make-safe and demolish electrical within lanb casework. Answered 5/5/2026 at 3:38 PM CDT by Marcus Howard

## Q117.  Laboratory Casework Responsibility

General Note A on sheet Q-104 states all laboratory casework, laboratory sinks, laboratory accessories, and laboratory service fixtures are Owner furnished and installed by Owner's laboratory casework vendor. However, the Owner's Special Conditions states that casework will be part of the Contractor scope of work. Please clarify.

Asked 4/15/2026 at 3:11 PM CDT

ANSWER Understood to be procured by UTSW, final connections and caulking to be by contractor. Answered 8/6/2026 at 9:03 PM CDT by Marcus Howard

## Q118.  AV-1 HDMI Plate

Keyed note 3/T-201 indicates to provide an HDMI plate and extension cable to D1 display. Please provide basis of design for AV-1 HDMI plate.

Asked 4/15/2026 at 3:10 PM CDT

ANSWER SSR: See detail of wall mounted display on T-501. AV specifications will be included to provide basis of design. Answered 8/6/2026 at 9:04 PM CDT by Marcus Howard

## Q119.  AV Cabling

Owner's Special Conditions, Part I Project Requirements states that General Contractor will provide AV cabling to existing telecom room to Owner-provided wall mounted displays. However, no AV drawings or specifications were provided. Please confirm AV cabling is by Contractor and, if so, please provide specifications.

Asked 4/15/2026 at 3:10 PM CDT

ANSWER SSR: UTSW is to provide cabeling and active components. Pathways and Raceways are to be provided by contractor. Confirmed that data cable scope is excluded from contractor's responsibile. Detail of wall mounted display is shown on sheet T-501. Answered 8/6/2026 at 9:05 PM CDT by Marcus Howard

## Q120.  Data Communications Cabling

Owner's Special Conditions, Part I Project Requirements states that data communications cabling demolition and installation will be furnished and installed by UTSW. However, data communications drawings and specifications were provided. Please confirm data cabling scope will be excluded from this contract, and Contractor is only responsible for raceways and boxes.

Asked 4/15/2026 at 3:10 PM CDT

ANSWER Refer to line item response 18. Answered 8/6/2026 at 9:05 PM CDT by Marcus Howard

## Q121.  O2 Sensor Location

Keyed note 13/EP-111 calls out an O2 sensor outside of Bio Hazard Waste 4.430K, and states to refer to mechanical drawings for rough-in location. Keyed note 7/MH-104 indicates the O2 sensor located outside of Cylinder Storage 4.430U. Please confirm the correct location for the O2 sensor is reflected on sheet MH-104.

Asked 4/15/2026 at 3:09 PM CDT

ANSWER SSR: Location shall be per mechanical drawings power can be coordinated to the correct location. O2 sensor shall read levels at the breathing zone of the bottle room. Answered 8/6/2026 at 9:05 PM CDT by Marcus Howard

## Q122.  New Electrical Circuits

Sheets ED-111 and ED-112: Please confirm reuse of existing conduit is acceptable for new circuits.

Asked 4/15/2026 at 3:09 PM CDT

ANSWER SSR: This needs to be confirm with UTSW if acceptable, SSR takes no exception as long as the conduits are not damaged and installation meets code. Answered 8/6/2026 at 9:05 PM CDT by Marcus Howard

## Q123.  TAB & Pre-Readings

Mechanical Demolition Note A on sheet M-001 states Contractor shall take air flow and static pressure readings on existing equipment before demolition. Does this requirement fall under the TAB scope? The Owner's Special Conditions indicates TAB should be excluded from Contractor's proposal. Please confirm TAB will be provided by Owner and, if so, please confirm Contractor is not responsible for the pre-demolition readings indicated in this note.

Asked 4/15/2026 at 3:08 PM CDT

ANSWER SSR: Needs to be addressed by UTSW PM. Pre-construction TAB verifications are typically on the contractor to coordinated. If owner is carrying project TAB then it is their ultimate decision on how to provide the pre-construction requests. Answered 8/6/2026 at 9:06 PM CDT by Marcus Howard

## Q124.  Sanitary Drip Pans

Keyed note 9 on sheet P-110 indicates a drip pan below waste piping. This keyed note appears to be pointing to a hatched line on the drawings, but is not called out at all locations where this hatched line occurs. Please confirm drip pans are required at all waste piping locations showing a hatched line, specifically in areas above operating rooms, equipment rooms, and Cath labs.

Asked 4/15/2026 at 3:08 PM CDT

ANSWER SSR: All outlined instances of piping are to be panned. This is over procedural or sterile storage areas. Keyed Note to be added to all areas. Answered 8/6/2026 at 9:06 PM CDT by Marcus Howard

## Q125.  Level 3 RCP

Please provide a reflected ceiling plan for Level 3, as this is required to coordinate underfloor plumbing scope.

Asked 4/15/2026 at 3:08 PM CDT

ANSWER UTSW to provide plans to contractor as requested. Answered 8/6/2026 at 9:17 PM CDT by Marcus Howard

## Q126.  Operating Room Wall Penetrations

Please provide wall penetration requirements at operating rooms for above ceiling plumbing work required on Level 3.

Asked 4/15/2026 at 3:07 PM CDT

ANSWER Utilize standard penetration details and procedures, scheduling needs to be done through UTSW on a case by case basis and after hours. For areas that are shielded additional procedures will need to utilize to maintain the integrity of the existing shield system. Answered 8/6/2026 at 9:18 PM CDT by Marcus Howard

## Q127.  Schedule of Level 3 OR Work

Please confirm OR operating schedule for above ceiling plumbing work required on Level 3.

Asked 4/15/2026 at 3:07 PM CDT

ANSWER Owner will need to be consulted for OR schedule coordination. Assume all work above active ORs is overtime/night work. Answered 8/6/2026 at 9:19 PM CDT by Marcus Howard

## Q128.  Crawl Space Confirmation

Please confirm whether there is a crawl space for below-slab sanitary waste pipe work on Level 1. If so, please provide UTSW Confined Space permitting requirements.

Asked 4/15/2026 at 3:06 PM CDT

ANSWER There is a crawl space below the level 01, As of the date of this response there are not specialized permit requirements for this space. Answered 8/6/2026 at 9:23 PM CDT by Marcus Howard

## Q129.  UTSW Commissioning Plan

Please provide UTSW commissioning plan for the project.

Asked 4/15/2026 at 3:06 PM CDT

ANSWER HDR to provide commissioning plan for AFB BSL-3 Lab space. UTSW to investigate further. Answered 8/6/2026 at 9:23 PM CDT by Marcus Howard

## Q130.  Systems Requiring Hot Tie-Ins Clarification

Per the pre-bid conference, it was indicated that tie-ins would be performed without outages. Does this apply to mechanical, plumbing, med gas, and electrical systems?

Asked 4/15/2026 at 3:06 PM CDT

ANSWER All electrical work will be hot-work. Mechanical and Plumbing shutdowns to be minimized with hot work when ever possible and be scheduled and approved by UTSW prior to preforming work. UTSW have the right to request hot work for any system on a case-by-case basis. Answered 8/6/2026 at 9:24 PM CDT by Marcus Howard

## Q131.  Panel Shutdowns

Per the pre-bid conference, it was indicated that no panel shutdowns are allowed, and all work must be hot work. Please confirm whether this requirement applies only to critical and life safety systems or all electrical power work. Will UTSW perform the electrical scope in hot electrical panels?

Asked 4/15/2026 at 3:05 PM CDT

ANSWER Contractor is required to preform all hot work. Contractor is to submit EEW for UTSW approval prior to preforming work. Answered 8/6/2026 at 9:26 PM CDT by Marcus Howard

## Q132.  HVAC System Cleaning Clarification

Specification Section 015719 references required cleaning for each HVAC unit and ductwork. Please clarify the extent of this requirement. Does this apply to only new work, or is this intended to apply to existing systems as well?

Asked 4/15/2026 at 3:04 PM CDT

ANSWER Duct cleaning is required if ductwork is not maintained per specifications during construction. Answered 8/6/2026 at 9:27 PM CDT by Marcus Howard

## Q133.  UTSW ICRA Policies

Please provide UTSW ICRA policies for airborne contaminant control referenced in Specification Section 015719.

Asked 4/15/2026 at 3:04 PM CDT

ANSWER Any hard panel wall system can be utilized as long as infection prevention requirements are met. Answered 8/6/2026 at 9:27 PM CDT by Marcus Howard

## Q134.  HEPA Filtered BSL-3 Exhaust

The Mechanical drawings do not appear to indicate any HEPA filtered BSL-3 exhaust until the exhaust fans (as noted in the schedule on sheet M-002). This is a cross contamination issue. Please advise. Contractor recommends using HEPA diffusers, or installing a bubble tight damper in exhaust at autoclave capture hoods that shut if the room goes positive to prevent cross contamination.

Asked 4/15/2026 at 3:03 PM CDT

ANSWER Recommend review of comment with ownership. Has operational implications that need to be studies. Note it is NOT recommended to put terminal HEPA at the bio-hazardous room, the moisture from the autoclaves is too close with no dilution. Answered 8/6/2026 at 9:29 PM CDT by Marcus Howard

## Q135.  Bubble Tight Dampers Confirmation

Keyed note 4/MH-104 indicates high speed, zero leakage, 120V motorized dampers to be utilized at BSL-3 supply and exhaust duct. Please confirm this note is referencing the bubble tight dampers indicated in Specification Section 233300, Part 2.7.

Asked 4/15/2026 at 3:03 PM CDT

ANSWER Correct Answered 8/6/2026 at 9:29 PM CDT by Marcus Howard

## Q136.  Supply Duct Contamination Issue

Sheet MH-104: The two (2) supply ducts branching off of the main 20"x20" SA between column lines 8.2 & 8.4 and L.3 & M are running to rooms outside of the BSL-3 containment boundary, which is a potential cross contamination issue. Please advise. Contractor recommends installing bubble tight dampers that shut to isolate at these tap locations.

Asked 4/15/2026 at 3:02 PM CDT

ANSWER Proceed with the design as-is. Recommendations will be evlauted with the Owner and Engineer Further Answered 8/6/2026 at 9:29 PM CDT by Marcus Howard

## Q137.  Exhaust Contamination Issue at Autoclaves

Sheet MH-104: The tap on exhaust that leads to Bio Hazard Waste 4.430K goes to the capture hoods at the autoclaves, which are outside the BSL-3 containment barrier. If the lab were to go positive, this could lead to a cross contamination issue. Please advise.

Asked 4/15/2026 at 3:02 PM CDT

ANSWER Proceed with the design as-is. Recommendations will be evaluated with the Owner and Engineer Further. Answered 8/6/2026 at 9:34 PM CDT by Marcus Howard

## Q138.  BSL-3 Research

What research is intended to take place in the BSL-3?

Asked 4/15/2026 at 3:01 PM CDT

ANSWER Not applicable for RFP response. Answered 8/6/2026 at 9:34 PM CDT by Marcus Howard

## Q139.  Sequence of Operations, BSL-3 Decontamination

Please advise if there is a sequence of operations for decontamination of the BSL-3 (AFB Lab).

Asked 4/15/2026 at 3:01 PM CDT

ANSWER Provide allowance for BSL-3 sequence of operations for controls sub-contractor. Recommendations will be evaluated with the Owner and Engineer Further. Answered 8/6/2026 at 9:35 PM CDT by Marcus Howard

## Q140.  BSL-3 Sequence of Operations In Exhaust Failure

Please advise if there is a sequence of operations for the BSL-3 (AFB Lab) in response to full exhaust fan failure.

Asked 4/15/2026 at 3:00 PM CDT

ANSWER Provide allowance for BSL-3 sequence of operations for controls sub-contractor. Recommendations will be evaluated with the Owner and Engineer Further Answered 8/6/2026 at 9:35 PM CDT by Marcus Howard

## Q141.  BSL-3 Sequence of Operations In Power Failure

Please advise if there is a sequence of operations for the BSL-3 (AFB Lab) in response to full building power failure.

Asked 4/15/2026 at 2:59 PM CDT

ANSWER Provide allowance for BSL-3 sequence of operations for controls sub-contractor. Recommendations will be evaluated with the Owner and Engineer Further. Answered 8/6/2026 at 9:36 PM CDT by Marcus Howard

## Q142.  Sequence of Operations, Hardwire Safeties

In the sequence of operations defined on sheet M-704, please elaborate on the hardwired safeties referred to in the following statement: "Exhaust fan system shall be stopped by any of the following: hardwired safeties".

Asked 4/15/2026 at 2:58 PM CDT

ANSWER Provide allowance for BSL-3 sequence of operations for controls sub-contractor. Recommendations will be evaluated with the Owner and Engineer Further. Answered 8/6/2026 at 9:37 PM CDT by Marcus Howard

## Q143.  BSL-3 Shutdown Sequence of Operations

On sheet M-704, please define the BSL-3 (AFB Lab) shutdown sequence of operations relative to both exhaust and supply.

Asked 4/15/2026 at 2:58 PM CDT

ANSWER Provide allowance for BSL-3 sequence of operations for controls sub-contractor. Recommendations will be evaluated with the Owner and Engineer Further. Answered 8/6/2026 at 9:37 PM CDT by Marcus Howard

## Q144.  BSL-3 Startup Sequence of Operations

On sheet M-704, please define the BSL-3 (AFB Lab) startup sequence of operations relative to both exhaust and supply. Exhaust should prove out before startup of supply.

Asked 4/15/2026 at 2:57 PM CDT

ANSWER Provide allowance for BSL-3 sequence of operations for controls sub-contractor. Recommendations will be evaluated with the Owner and Engineer Further. Answered 8/6/2026 at 9:38 PM CDT by Marcus Howard

## Q145.  Sequence of Operations, Exhaust Interlock

In the sequence of operations defined on sheet M-702, please elaborate on the following statement: "Interlocked exhaust fans shall start/stop via hardwire interlock with supply." Typically, supply is interlocked with exhaust for exhaust failure. If supply fails, exhaust should continue to run, maintaining directional airflow requirements until the lab can initiate appropriate SOP's for biosafety, and then shut down. Typically, exhaust is run for a timed period to allow for safe shutdown of the lab.

Asked 4/15/2026 at 2:56 PM CDT

ANSWER Provide allowance for BSL-3 sequence of operations for controls sub-contractor. Recommendations will be evaluated with the Owner and Engineer Further Answered 8/6/2026 at 9:39 PM CDT by Marcus Howard

## Q146.  Missing Docs

Missing from specs: 08 80 00 and 21 05 00.

Asked 4/7/2026 at 1:53 PM CDT

ANSWER 21 05 00 Provided on Specifications date 4/11/26. Answered 4/24/2026 at 3:11 PM CDT by Marcus Howard

## Q147.  Alternates

In the drawings it shows Alt#5 is for Aquatap water system but there is nothing in the specs about it. Is this something we need to include in our pricing?

Asked 4/7/2026 at 1:34 PM CDT

ANSWER Aquatap product to be priced as an alternate to the full DI/RO loop shown in design. Aquatap is a product that prevents the need to bring full loop for DI/RO down the wall near the sinks. Answered 4/24/2026 at 3:15 PM CDT by Marcus Howard

## Q148.  Responsibility Matix

We just had a few questions on who is responsible for these items? Signage (preferred vender?) Fire Alarm (Vendor?) Low Voltage Controls Testing/Inspections TAB (preferred vendor?)

Asked 4/7/2026 at 1:33 PM CDT

ANSWER "Signage (UTSW) Fire Alarm: (Contractor will hire fire alarm contractor) Low Voltage: (Contractor will hire Siemens), TAB (UTSW will hire EAB)" Answered 4/24/2026 at 3:15 PM CDT by Marcus Howard

## Q149.  Site Walk Sign-in sheet

Good Day, Can we ask a copy of the site-walk sign in sheet? Thank you in advance!

Asked 4/7/2026 at 12:49 PM CDT

ANSWER The copy of the sign in sheet can be found in the Pre-Requisite section of the RFP. Answered 4/24/2026 at 3:16 PM CDT by Marcus Howard

## Q150.  CUH 4.219

Is this RFP for a General Contractor

Asked 4/6/2026 at 10:55 PM CDT

ANSWER Yes Answered 4/24/2026 at 3:16 PM CDT by Marcus Howard

## Q151.  Prebid Meeting SIS

Is a prebid meeting sign in sheet available?

Asked 4/6/2026 at 9:46 AM CDT

ANSWER The sign in sheet can be found in the pre-requisite section of the RFP. Answered 4/24/2026 at 3:17 PM CDT by Marcus Howard

## Q152.  EST

Is an estimated cost available?

Asked 4/6/2026 at 9:45 AM CDT

ANSWER Not at this time. Estimated cost will be provided after the awarding of the RFP. Answered 4/24/2026 at 3:18 PM CDT by Marcus Howard

## Q153.  Commissioning

Reviewing the project manual, it notes that the project will require commissioning. What is the process for proposing on the commissioning for this project?

Asked 3/24/2026 at 3:17 PM CDT

ANSWER Commissioning requirements 01 91 00 can be found in the pre-requisite section of the RFP. Answered 4/24/2026 at 3:20 PM CDT by Marcus Howard